# A001-CMR-2026-08 — Condition Monitoring Report

Synthetic training document. This Markdown file is a browseable text mirror of the original PDF used in the ENEC 2026 A-001 RAG corpus. The original PDF is included in the companion data/PDF download pack.

<PARSED TEXT FOR PAGE: 1 / 2>NORTHSTAR PROCESS FACILITY SYNTHETIC TRAINING CORPUS A001-CMR-2026-08 | APPROVED | Synthetic training document - not for operational use Page 1 A001-CMR-2026-08 / APPROVED A-001 Monthly Condition Monitoring Report - August 2026 A-001 | Cooling Water Pump | Enterprise Asset Reliability Training Scenario Document ID A001-CMR-2026-08 Version 1.0 Status APPROVED Effective / Issue Date 2026-08-25 Owner Condition Monitoring Team Asset A-001 Location Utilities Area - Bay 3 Data Class Synthetic / Training TRAINING NOTICE: This fictional document is designed only for AI/RAG, analytics and governance training. It is not an engineering instruction and must not be used on real equipment. 1. Executive Summary The August training dataset shows a sustained increase in A-001 vibration compared with its earlier-month baseline. Bearing temperature remains variable but does not show the same monotonic pattern. The asset also has multiple open work orders. The combined evidence supports a qualified review; this report does not identify a confirmed failure mode. 2. Trend Snapshot Date Vibration RMS (mm/s) Bearing Temp (C) Comment 2026-08-12 3.8 67 Earlier-month baseline sample 2026-08-15 4.4 69 Gradual increase 2026-08-18 5.1 70 Trend persists 2026-08-21 5.8 71 Inspection requested 2026-08-24 6.4 72 Higher than earlier-month baseline 2026-08-25 6.6 71 Latest report sample 3. Related Work Work order Priority Status Summary WO-2026-0817 HIGH OPEN Inspect elevated vibration indication WO-2026-0729 MEDIUM IN PROGRESS Review coupling/alignment observation history WO-2026-0612 LOW CLOSED Routine lubrication inspection<PARSED TEXT FOR PAGE: 2 / 2>NORTHSTAR PROCESS FACILITY SYNTHETIC TRAINING CORPUS A001-CMR-2026-08 | APPROVED | Synthetic training document - not for operational use Page 2 4. Findings  The vibration trend is the strongest consistent signal in the report period.  The temperature signal varies within a narrower band and does not independently establish the same trend.  Open maintenance work means the condition should not be interpreted independently of work history.  No single record in this report establishes root cause. 5. Recommendation Apply A001-PROC-INS-001-V2, verify sensor quality, review the open inspection work order, compare the latest observation with prior findings and request qualified reliability review. Record any evidence gap or conflicting observation. 6. Source Notes All numbers are synthetic and intentionally simplified for AI training. The report is designed to support hybrid RAG questions that combine narrative findings with structured asset and work-order data. 7. Evidence Traceability Claim Supporting source Vibration increased through the sampled August window Trend Snapshot in this report / sensor_readings Multiple maintenance items remain active Related Work / work_orders Inspection was requested WO-2026-0817 Current formal review workflow is version 2.0 A001-PROC-INS-001-V2 8. Open Questions for Review  Does the full-resolution sensor history show the same pattern as the sampled values?  Are any recent maintenance activities temporally aligned with the change?  Does the field observation on 2026-08-19 corroborate or conflict with the instrumented trend?  Is any required evidence missing before the case can be classified? 9. Reviewer Sign-off Role Status Condition Monitoring Reviewer Report issued Maintenance / Reliability Reviewer Pending review Work-order close-out Not complete